## Slide 1
WBMS-SWLT 16S 80A
Smart BMS Manages Lithium Ion Batteries
with Precision and Speed
Specification Sheet v1.0

## Slide 2
Application Diagram
Application Diagram
NISO CAN2.0B
RS232 RS485

## Slide 3
Scalable up to 8 cells & 12-24V battery packs
Multiple communication options: Non-Isolated CAN 2.0, RS232 and RS485
High side N-MOSFET control provides safe and uninterrupted ground connection to external subsystems.
Predischarge control for preventing inrush currents to capacitive loads. Prevents MOSFET failures and increases cell life
Short Circuit and Overcurrent in discharge latches ensure automatic locking of discharge path after repeated short circuit and overcurrent faults
Cell balancing current up to 120mA minimizes cell to cell voltage and SOC variations and optimal charging of battery pack
Individual Cell over and under voltage and temperature protection
Pack level over current and short circuit protection
Deep Discharge Prevention (Auto BMS Shutdown) when cell voltage is critically low
Proprietary CAN based field servicing tools for data monitoring, logging and firmware update
Salient Features

## Slide 4
Specifications |  |  | Remarks
Number of Cells |  | Min: 4 Max: 8 | 
Cell Voltage Sensing Range |  | 1.6 - 4.5V | 
Peak Battery Terminal Voltage |  | 33.6 V (8S) | 
Sensing Accuracy |  | Cell Voltage: ±3mV Current: ±1% | 
Dimension |  | 155 mm X 70 mm X 16 mm (L X B X H) | 
Rated Nominal Continuous Current Rating | Charging and Discharging Current | Up to 80A. Needs thermal connection to metal battery pack casing for PDU heat dissipation to maintain continuous current rating. Continuous current rating to be derated to ~65% of the rated value if no thermal connection is present. | 
Cell Balancing | Balancing Current per Cell | ~150 mA | 
Pre-discharge control | Nominal Capacitive load | 3-6mF in 0.5 seconds | 
Temperature Sensing | Onboard | One channel for onboard MOSFET temperature | 
 | External | Two external channels for cell temperature | 
 | Range and Accuracy | Range: -10℃ to 120℃ Accuracy ±1℃, | 
Over Voltage Protection | Threshold, Protection Trigger Delay | Configurable | Configurable, based on target fully charged voltage
 | Fault Response | Charge MOSFET: OFF, Discharge MOSFET: ON | 
 | Fault Release | Through Hysteresis, Automatic | 
Under Voltage Protection | Threshold, Protection Trigger Delay | Configurable | Configurable, based on target fully charged voltage
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: ON | 
 | Fault Release | Configurable Hysteresis | No load removal required. Charging current is allowed.
Over Current in Discharge Protection Level-1 | Threshold, Protection Trigger Delay | Configurable to allow up to 100A discharge for up to 60 seconds | Configurable
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: ON | 
 | Fault Release | Auto recovery after no discharge current for 90 secs | 
Over Current in Discharge Protection Level-2 | Threshold, Protection Trigger Delay | Configurable to instantaneously cut off at 120A discharge current in 100 mSec | 
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: ON | 
 | Fault Release | Auto recovery after no discharge current for 90 secs | 
Note: Specifications are indicative only. Final specifications and behaviour including continuous discharge/charge current, balancing current, protection thresholds, etc. may vary depending upon BMS version, BMS mounting scheme, PDU heat dissipation, programmed parameters and application logic.

## Slide 5
Specifications |  |  | Remarks
Over Current in Discharge Latch Protection | Threshold | 5 consecutive over discharge current faults | 
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: ON | 
 | Fault Release | Load Removal or Auto release | 
Over Current in Charge Protection Level-1 | Threshold, Protection Trigger Delay | Configurable to allow up to 100A charge current for up to 60 seconds | Configurable
 | Fault Response | Discharge MOSFET: ON, Charge MOSFET: OFF | 
 | Fault Release | Auto recovery after no charge current for 90 secs | 
Over Current in Charge Protection Level-2 | Threshold, Protection Trigger Delay | Configurable to instantaneously cut off at 120A charge current in 100 mSec | 
 | Fault Response | Charge MOSFET: OFF, Discharge MOSFET: ON | 
 | Fault Release | Auto recovery after no charge current for 90 secs | 
Short Circuit in Discharge Protection | Protection Trigger Delay | ～30 uSec | 
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: OFF | 
 | Fault Release | Auto recovery after 5 seconds | 
Short Circuit in Discharge Latch Protection | Threshold | 2 consecutive short circuit faults | 
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: OFF | 
 | Fault Release | Load Removal | 
Over Temperature in Discharge Protection | Threshold, Protection Trigger Delay | Configurable | Configurable
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: ON | 
 | Fault Release | Auto recovery below configurable temperature | 
Under Temperature in Discharge Protection | Threshold, Protection Trigger Delay | Configurable | Configurable
 | Fault Response | Discharge MOSFET: OFF, Charge MOSFET: ON | 
 | Fault Release | Auto recovery above configurable temperature | 
Over Temperature in Charge Protection | Threshold, Protection Trigger Delay | Configurable | Configurable
 | Fault Response | Charge MOSFET: OFF, Discharge MOSFET: ON | 
 | Fault Release | Auto recovery below configurable temperature | 
Under Temperature in Charge Protection | Threshold, Protection Trigger Delay | Configurable | Configurable
 | Fault Response | Charge MOSFET: OFF, Discharge MOSFET: ON | 
 | Fault Release | Auto recovery above configurable temperature |